## Tabelle1
Info: AT %Q* stands for outgoing values from PLC perspective AT %I* represent data points accepting external signals incoming Mirrored values are internal values usually used in the auto mode of the systems or simply variables that are processed merely in the auto mode
//Mirrored mode values for ADS reading
eModeMainControlModeADSmirror | AT %Q* | : E_ControlMode;
eModeDHSADSmirror | AT %Q* | : E_ControlMode;
eModeCCAADSmirror | AT %Q* | : E_ControlMode;
eModeCPHADSmirror | AT %Q* | : E_ControlMode;
eModeDIDHADSmirror | AT %Q* | : E_ControlMode;
eModeDIDCADSmirror | AT %Q* | : E_ControlMode;
eModeAHUADSmirror | AT %Q* | : E_ControlMode;
eModeJNADSmirror | AT %Q* | : E_ControlMode;
eModeEHAADSmirror | AT %Q* | : E_ControlMode;
eModeBATBATHADSmirror | AT %Q* | : E_ControlMode;
eModeRHARCADSmirror | AT %Q* | : E_ControlMode;
//District heating station datapoints
//Temperature sensor datapoints
fDHSTempSupPrimADS | AT %Q* | : REAL;
fDHSTempRetPrimADS | AT %Q* | : REAL;
//DHS power setpoint
fDHSPowSetADS | AT %I* | : REAL;
//Mirrored DHS power value for ADS reading
fDHSPowSetADSmirror | AT %Q* | : REAL;
//Concrete core activation datapoints
//Temperature sensor datapoints
fCCATempSupPrimADS | AT %Q* | : REAL;
fCCATempRetPrimADS | AT %Q* | : REAL;
fCCATempSupADS | AT %Q* | : REAL;
fCCATempRetADS | AT %Q* | : REAL;
//Valve datapoints
fCCAValveActADS | AT %Q* | : REAL;
fCCAValveSetADS | AT %I* | : REAL;
//Mirrored CCA valve value for ADS reading
fCCAValveSetADSmirror | AT %Q* | : REAL;
//Pump datapoints
eCCAPumpContModeADS | AT %I* | : E_PumpControlMode;
//Mirrored CCA pump mode value for ADS reading
eCCAPumpContModeADSmirror | AT %Q* | : E_PumpControlMode;
bCCAPumpErrorADS | AT %Q* | : BOOL;
bCCAPumpOperatingADS | AT %Q* | : BOOL;
fCCAPumpPowerADS | AT %Q* | : REAL;
fCCAPumpPressureADS | AT %Q* | : REAL;
bCCAPumpSetOnADS | AT %Q* | : BOOL;
fCCAPumpSetpointADS | AT %I* | : REAL;
//Mirrored CCA pump set point value for ADS reading
fCCAPumpSetpointADSmirror | AT %Q* | : REAL;
fCCAPumpSpeedADS | AT %Q* | : REAL;
fCCAPumpVolFlowADS | AT %Q* | : REAL;
//Cealing panel heater datapoints
//Temperature sensor datapoints
fCPHTempSupPrimADS | AT %Q* | : REAL;
fCPHTempRetPrimADS | AT %Q* | : REAL;
fCPHTempSupADS | AT %Q* | : REAL;
fCPHTempRetADS | AT %Q* | : REAL;
//Valve datapoints
fCPHMixValveActADS | AT %Q* | : REAL;
fCPHMixValveSetADS | AT %I* | : REAL;
fCPHMixValveSetADSmirror | AT %Q* | : REAL;
fCPHThrotValveActADS | AT %Q* | : REAL;
fCPHThrotValveSetADS | AT %I* | : REAL;
fCPHThrotValveSetADSmirror | AT %Q* | : REAL;
//Pump datapoints
eCPHPumpContModeADS | AT %I* | : E_PumpControlMode;
eCPHPumpContModeADSmirror | AT %Q* | : E_PumpControlMode;
bCPHPumpErrorADS | AT %Q* | : BOOL;
bCPHPumpOperatingADS | AT %Q* | : BOOL;
fCPHPumpPowerADS | AT %Q* | : REAL;
fCPHPumpPressureADS | AT %Q* | : REAL;
bCPHPumpSetOnADS | AT %Q* | : BOOL;
fCPHPumpSetpointADS | AT %I* | : REAL;
fCPHPumpSetpointADSmirror | AT %Q* | : REAL;
fCPHPumpSpeedADS | AT %Q* | : REAL;
fCPHPumpVolFlowADS | AT %Q* | : REAL;
//DID (cealing induction unit/chilled beam) heating datapoints
//Temperature sensor datapoints
fDIDHTempSupPrimADS | AT %Q* | : REAL;
fDIDHTempRetPrimADS | AT %Q* | : REAL;
fDIDHTempSupADS | AT %Q* | : REAL;
fDIDHTempRetADS | AT %Q* | : REAL;
//Valve datapoints
fDIDHValveActADS | AT %Q* | : REAL;
fDIDHValveSetADS | AT %I* | : REAL;
fDIDHValveSetADSmirror | AT %Q* | : REAL;
//Pump datapoints
eDIDHPumpContModeADS | AT %I* | : E_PumpControlMode;
eDIDHPumpContModeADSmirror | AT %Q* | : E_PumpControlMode;
bDIDHPumpErrorADS | AT %Q* | : BOOL;
bDIDHPumpOperatingADS | AT %Q* | : BOOL;
fDIDHPumpPowerADS | AT %Q* | : REAL;
fDIDHPumpPressureADS | AT %Q* | : REAL;
bDIDHPumpSetOnADS | AT %Q* | : BOOL;
fDIDHPumpSetpointADS | AT %I* | : REAL;
fDIDHPumpSetpointADSmirror | AT %Q* | : REAL;
fDIDHPumpSpeedADS | AT %Q* | : REAL;
fDIDHPumpVolFlowADS | AT %Q* | : REAL;
//DID (ceiling induction unit/chilled beam) cooling datapoints
//Temperature sensor datapoints (
fDIDCTempSupPrimADS | AT %Q* | : REAL;
fDIDCTempRetPrimADS | AT %Q* | : REAL;
fDIDCTempSupADS | AT %Q* | : REAL;
fDIDCTempRetADS | AT %Q* | : REAL;
//Valve datapoints
fDIDCValveActADS | AT %Q* | : REAL;
fDIDCValveSetADS | AT %I* | : REAL;
fDIDCValveSetADSmirror | AT %Q* | : REAL;
//Pump datapoints
eDIDCPumpContModeADS | AT %I* | : E_PumpControlMode;
eDIDCPumpContModeADSmirror | AT %Q* | : E_PumpControlMode;
bDIDCPumpErrorADS | AT %Q* | : BOOL;
bDIDCPumpOperatingADS | AT %Q* | : BOOL;
fDIDCPumpPowerADS | AT %Q* | : REAL;
fDIDCPumpPressureADS | AT %Q* | : REAL;
bDIDCPumpSetOnADS | AT %Q* | : BOOL;
fDIDCPumpSetpointADS | AT %I* | : REAL;
fDIDCPumpSetpointADSmirror | AT %Q* | : REAL;
fDIDCPumpSpeedADS | AT %Q* | : REAL;
fDIDCPumpVolFlowADS | AT %Q* | : REAL;
//RHAndRC
//Temperature sensor datapoints
fRHARCRCTempSupPrimADS | AT %Q* | : REAL;
fRHaRCRCTempRetPrimADS | AT %Q* | : REAL;
fRHARCRCTempSupADS | AT %Q* | : REAL;
fRHARCRCTempRetADS | AT %Q* | : REAL;
//Valve datapoints
fRHARCThrotValveActADS | AT %Q* | : REAL;
fRHARCThrotValveSetADS | AT %I* | : REAL;
fRHARCThrotValveSetADSmirror | AT %Q* | : REAL;
//Three-way-Valve datapoints
fRHARCSwitchValveSupActADS | AT %Q* | : REAL;
fRHARCSwitchValveSupSetADS | AT %I* | : REAL;
fRHARCSwitchValveSupSetADSmirror | AT %Q* | : REAL;
fRHARCSwitchValveRetActADS | AT %Q* | : REAL;
fRHARCSwitchValveRetSetADS | AT %I* | : REAL;
fRHARCSwitchValveRetSetADSmirror | AT %Q* | : REAL;
//Pump datapoints
eRHARCPumpContModeADS | AT %I* | : E_PumpControlMode;
eRHARCPumpContModeADSmirror | AT %Q* | : E_PumpControlMode;
bRHaRCPumpErrorADS | AT %Q* | : BOOL;
bRHARCPumpOperatingADS | AT %Q* | : BOOL;
fRHARCPumpPowerADS | AT %Q* | : REAL;
fRHARCPumpPressureADS | AT %Q* | : REAL;
bRHARCPumpSetOnADS | AT %Q* | : BOOL;
fRHARCPumpSetpointADS | AT %I* | : REAL;
fRHARCPumpSetpointADSmirror | AT %Q* | : REAL;
fRHARCPumpSpeedADS | AT %Q* | : REAL;
fRHARCPumpVolFlowADS | AT %Q* | : REAL;
//Jet nozzle datapoints
//Volume flow controller datapoints
fJNVolumeFlowSetpoint1ADS | AT %I* | : REAL;
//fJNVolumeFlowSetpoint2ADS | AT %I* | : REAL; |  | //Dismantled
fJNVolumeFlowSetpoint3ADS | AT %I* | : REAL;
//fJNVolumeFlowSetpoint4ADS | AT %I* | : REAL; |  | //Dismantled
fJNVolumeFlowSetpoint5ADS | AT %I* | : REAL;
fJNVolumeFlowSetpoint6ADS | AT %I* | : REAL;
fJNVolumeFlowSetpoint7ADS | AT %I* | : REAL;
fJNVolumeFlowSetpoint8ADS | AT %I* | : REAL;
fJNVolumeFlowSetpoint9ADS | AT %I* | : REAL;
fJNVolumeFlowSetpoint10ADS | AT %I* | : REAL;
fJNVolumeFlowSetpoint1ADSmirror | AT %Q* | : REAL;
//fJNVolumeFlowSetpoint2ADSmirror | AT %Q* | : REAL; |  | //Dismantled
fJNVolumeFlowSetpoint3ADSmirror | AT %Q* | : REAL;
//fJNVolumeFlowSetpoint4ADSmirror | AT %Q* | : REAL; |  | //Dismantled
fJNVolumeFlowSetpoint5ADSmirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint6ADSmirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint7ADSmirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint8ADSmirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint9ADSmirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint10ADSmirror | AT %Q* | : REAL;
fJNVolumeFlowActual1ADS | AT %Q* | : REAL;
//fJNVolumeFlowActual2ADS | AT %Q* | : REAL; |  | //Dismantled
fJNVolumeFlowActual3ADS | AT %Q* | : REAL;
//fJNVolumeFlowActual4ADS | AT %Q* | : REAL; |  | //Dismantled
fJNVolumeFlowActual5ADS | AT %Q* | : REAL;
fJNVolumeFlowActual6ADS | AT %Q* | : REAL;
fJNVolumeFlowActual7ADS | AT %Q* | : REAL;
fJNVolumeFlowActual8ADS | AT %Q* | : REAL;
fJNVolumeFlowActual9ADS | AT %Q* | : REAL;
fJNVolumeFlowActual10ADS | AT %Q* | : REAL;
//Angle datapoints
fJNAngleSetpoint1ADS | AT %I* | : REAL;
//fJNAngleSetpoint2ADS | AT %I* | : REAL; |  | //Dismantled
fJNAngleSetpoint3ADS | AT %I* | : REAL;
//fJNAngleSetpoint4ADS | AT %I* | : REAL; |  | //Dismantled
fJNAngleSetpoint5ADS | AT %I* | : REAL;
fJNAngleSetpoint6ADS | AT %I* | : REAL;
fJNAngleSetpoint7ADS | AT %I* | : REAL;
fJNAngleSetpoint8ADS | AT %I* | : REAL;
fJNAngleSetpoint9ADS | AT %I* | : REAL;
fJNAngleSetpoint10ADS | AT %I* | : REAL;
fJNAngleSetpoint1ADSmirror | AT %Q* | : REAL;
//fJNAngleSetpoint2ADSmirror | AT %Q* | : REAL; |  | //Dismantled
fJNAngleSetpoint3ADSmirror | AT %Q* | : REAL;
//fJNAngleSetpoint4ADSmirror | AT %Q* | : REAL; |  | //Dismantled
fJNAngleSetpoint5ADSmirror | AT %Q* | : REAL;
fJNAngleSetpoint6ADSmirror | AT %Q* | : REAL;
fJNAngleSetpoint7ADSmirror | AT %Q* | : REAL;
fJNAngleSetpoint8ADSmirror | AT %Q* | : REAL;
fJNAngleSetpoint9ADSmirror | AT %Q* | : REAL;
fJNAngleSetpoint10ADSmirror | AT %Q* | : REAL;
fJNAngleActual1ADS | AT %Q* | : REAL;
//fJNAngleActual2ADS | AT %Q* | : REAL; |  | //Dismantled
fJNAngleActual3ADS | AT %Q* | : REAL;
//fJNAngleActual4ADS | AT %Q* | : REAL; |  | //Dismantled
fJNAngleActual5ADS | AT %Q* | : REAL;
fJNAngleActual6ADS | AT %Q* | : REAL;
fJNAngleActual7ADS | AT %Q* | : REAL;
fJNAngleActual8ADS | AT %Q* | : REAL;
fJNAngleActual9ADS | AT %Q* | : REAL;
fJNAngleActual10ADS | AT %Q* | : REAL;
//Hall 1 central exhaust air datapoints
//Volume flow controller datapoints
fEHAVolumeFlowSetpoint1ADS | AT %I* | : REAL;
fEHAVolumeFlowSetpoint2ADS | AT %I* | : REAL;
fEHAVolumeFlowSetpoint1ADSmirror | AT %Q* | : REAL;
fEHAVolumeFlowSetpoint2ADSmirror | AT %Q* | : REAL;
fEHAVolumeFlowActual1ADS | AT %Q* | : REAL;
fEHAVolumeFlowActual2ADS | AT %Q* | : REAL;
//Air handling unit datapoints
//Flap datapoints
fAHUFlapEHAActADS | AT %Q* | : REAL;
fAHUFlapEHASetADS | AT %I* | : REAL;
fAHUFlapEHASetADSmirror | AT %Q* | : REAL;
fAHUFlapETAActADS | AT %Q* | : REAL;
fAHUFlapETASetADS | AT %I* | : REAL;
fAHUFlapETASetADSmirror | AT %Q* | : REAL;
fAHUFlapODAActADS | AT %Q* | : REAL;
fAHUFlapODASetADS | AT %I* | : REAL;
fAHUFlapODASetADSmirror | AT %Q* | : REAL;
fAHUFlapSUPActADS | AT %Q* | : REAL;
fAHUFlapSUPSetADS | AT %I* | : REAL;
fAHUFlapSUPSetADSmirror | AT %Q* | : REAL;
//Fan datapoints
fAHUFanETASpeedActADS | AT %Q* | : REAL;
fAHUFanETASpeedSetADS | AT %I* | : REAL;
fAHUFanETASpeedSetADSmirror | AT %Q* | : REAL;
fAHUFanETAVdpActADS | AT %Q* | : REAL;
fAHUFanETAVolFlowActADS | AT %Q* | : REAL;
fAHUFanSUPSpeedActADS | AT %Q* | : REAL;
fAHUFanSUPSpeedSetADS | AT %I* | : REAL;
fAHUFanSUPSpeedSetADSmirror | AT %Q* | : REAL;
fAHUFanSUPVdpActADS | AT %Q* | : REAL;
fAHUFanSUPVolFlowActADS | AT %Q* | : REAL;
//Temperature sensor datapoints
//fAHUTempAmbAirADS | AT %Q* | : REAL;
fAHUTempEHAADS | AT %Q* | : REAL;
fAHUTempETAADS | AT %Q* | : REAL;
fAHUTempODAADS | AT %Q* | : REAL;
fAHUTempSUPADS | AT %Q* | : REAL;
//Humidity sensor datapoints
fAHUHumEHAADS | AT %Q* | : REAL;
fAHUHumETAADS | AT %Q* | : REAL;
fAHUHumODAADS | AT %Q* | : REAL;
fAHUHumSUPADS | AT %Q* | : REAL;
//Frost protection sensor datapoints
bAHUFrostProtADS | AT %Q* | : BOOL;
//Preheater datapoints
//Temperature sensor datapoints
fAHUPHTempSupPrimADS | AT %Q* | : REAL;
fAHUPHTempRetPrimADS | AT %Q* | : REAL;
fAHUPHTempSupADS | AT %Q* | : REAL;
fAHUPHTempRetADS | AT %Q* | : REAL;
//Valve datapoints
fAHUPHValveActADS | AT %Q* | : REAL;
fAHUPHValveSetADS | AT %I* | : REAL;
fAHUPHValveSetADSmirror | AT %Q* | : REAL;
//Pump datapoints
eAHUPHPumpContModeADS | AT %I* | : E_PumpControlMode;
eAHUPHPumpContModeADSmirror | AT %Q* | : E_PumpControlMode;
bAHUPHPumpErrorADS | AT %Q* | : BOOL;
bAHUPHPumpOperatingADS | AT %Q* | : BOOL;
fAHUPHPumpPowerADS | AT %Q* | : REAL;
fAHUPHPumpPressureADS | AT %Q* | : REAL;
bAHUPHPumpSetOnADS | AT %Q* | : BOOL;
fAHUPHPumpSetpointADS | AT %I* | : REAL;
fAHUPHPumpSetpointADSmirror | AT %Q* | : REAL;
fAHUPHPumpSpeedADS | AT %Q* | : REAL;
fAHUPHPumpVolFlowADS | AT %Q* | : REAL;
//Heat recovery datapoints
fAHUHRBypValveAct1ADS | AT %Q* | : REAL;
fAHUHRBypValveAct2ADS | AT %Q* | : REAL;
fAHUHRBypValveSetADS | AT %I* | : REAL;
fAHUHRBypValveSetADSmirror | AT %Q* | : REAL;
fAHUHRTempOutEstimatedADS | AT %Q* | : REAL;
//Cooler datapoints
//Temperature sensor datapoints
fAHUCOTempSupPrimADS | AT %Q* | : REAL;
fAHUCOTempRetPrimADS | AT %Q* | : REAL;
fAHUCOTempSupADS | AT %Q* | : REAL;
fAHUCOTempRetADS | AT %Q* | : REAL;
fAHUCOTempOutSetADS | AT %I* | : REAL;
fAHUCOTempOutSetADSmirror | AT %Q* | : REAL;
fAHUCOTempOutEstimatedADS | AT %Q* | : REAL;
//Valve datapoints
fAHUCOValveActADS | AT %Q* | : REAL;
fAHUCOValveSetADS | AT %I* | : REAL;
fAHUCOValveSetADSmirror | AT %Q* | : REAL;
//Pump datapoints
eAHUCOPumpContModeADS | AT %I* | : E_PumpControlMode;
eAHUCOPumpContModeADSmirror | AT %Q* | : E_PumpControlMode;
bAHUCOPumpErrorADS | AT %Q* | : BOOL;
bAHUCOPumpOperatingADS | AT %Q* | : BOOL;
fAHUCOPumpPowerADS | AT %Q* | : REAL;
fAHUCOPumpPressureADS | AT %Q* | : REAL;
bAHUCOPumpSetOnADS | AT %Q* | : BOOL;
fAHUCOPumpSetpointADS | AT %I* | : REAL;
fAHUCOPumpSetpointADSmirror | AT %Q* | : REAL;
fAHUCOPumpSpeedADS | AT %Q* | : REAL;
fAHUCOPumpVolFlowADS | AT %Q* | : REAL;
//Reheater datapoints
//Temperature sensor datapoints
fAHURHTempSupPrimADS | AT %Q* | : REAL;
fAHURHTempRetPrimADS | AT %Q* | : REAL;
fAHURHTempSupADS | AT %Q* | : REAL;
fAHURHTempRetADS | AT %Q* | : REAL;
//Valve datapoints
fAHURHValveActADS | AT %Q* | : REAL;
fAHURHValveSetADS | AT %I* | : REAL;
fAHURHValveSetADSmirror | AT %Q* | : REAL;
//Pump datapoints
eAHURHPumpContModeADS | AT %I* | : E_PumpControlMode;
eAHURHPumpContModeADSmirror | AT %Q* | : E_PumpControlMode;
bAHURHPumpErrorADS | AT %Q* | : BOOL;
bAHURHPumpOperatingADS | AT %Q* | : BOOL;
fAHURHPumpPowerADS | AT %Q* | : REAL;
fAHURHPumpPressureADS | AT %Q* | : REAL;
bAHURHPumpSetOnADS | AT %Q* | : BOOL;
fAHURHPumpSetpointADS | AT %I* | : REAL;
fAHURHPumpSetpointADSmirror | AT %Q* | : REAL;
fAHURHPumpSpeedADS | AT %Q* | : REAL;
fAHURHPumpVolFlowADS | AT %Q* | : REAL;
//SteamHumidifier datapoints
fAHUSHSetpointADS | AT %I* | : REAL;
fAHUSHSetpointADSmirror | AT %Q* | : REAL;
//Battery ventilation datapoints
//BAT power setpoints
fBATSupSetADS | AT %I* | : REAL;
fBATEhaSetADS | AT %I* | : REAL;
fBATSupSetADSmirror | AT %Q* | : REAL;
fBATEhaSetADSmirror | AT %Q* | : REAL;
//Bathroom ventilation datapoints
//BATH power setpoint
fBATHSupActADS | AT %Q* | : REAL;
fBATHSupSetADS | AT %I* | : REAL;
fBATHEhaSetADS | AT %I* | : REAL;
fBATHSupSetADSmirror | AT %Q* | : REAL;
fBATHEhaSetADSmirror | AT %Q* | : REAL;
//Hall 2 datapoints
(*
nHALL2TempRoom | AT %I* | : INT;
bHALL2LED | AT %Q* | : BOOL | := 0;
bHALL2Button | AT %I* | : BOOL;
nHALL2TempOffset | AT %I* | : INT;
nHALL2Radiation | AT %I* | : INT;
*)
//Mirror all internal variables
//Ambient air datapoints
fTemperatureAmbientADSmirror | AT %Q* | : REAL;
//District heating station datapoints
//Temperature sensor datapoints
fDHSTempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fDHSTempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
//DHS power setpoint
fDHSPowSetADSInternalValuesMirror | AT %Q* | : REAL;
fDHSSafetyMarginADSInternalValuesMirror | AT %Q* | : REAL; |  | //additional safety margin in case, the DHS has a decreased supply temperature
//DCS pump
eDCSPumpContModeADSInternalValuesMirror | AT %Q* | : INT;
fDCSPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
bDCSPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fDCSPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fDCSPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
eDCSPumpOpModeADSInternalValuesMirror | AT %Q* | : INT;
fDCSPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fDCSPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
//Concrete core activation datapoints
//Temperature sensor datapoints
fCCATempSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fCCATempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fCCATempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
fCCATempSupADSInternalValuesMirror | AT %Q* | : REAL;
fCCATempRetADSInternalValuesMirror | AT %Q* | : REAL;
//Valve datapoints
bCCAValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fCCAValveActADSInternalValuesMirror | AT %Q* | : REAL;
fCCAValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Pump datapoints
eCCAPumpContModeADSInternalValuesMirror | AT %Q* | : E_PumpControlMode;
bCCAPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
bCCAPumpOperatingADSInternalValuesMirror | AT %Q* | : BOOL;
fCCAPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fCCAPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
bCCAPumpSetOnADSInternalValuesMirror | AT %Q* | : BOOL;
fCCAPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fCCAPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
fCCAPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
//Cealing panel heater datapoints
//Temperature sensor datapoints
fCPHTempSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fCPHTempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fCPHTempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
fCPHTempSupADSInternalValuesMirror | AT %Q* | : REAL;
fCPHTempRetADSInternalValuesMirror | AT %Q* | : REAL;
//Valve datapoints
bCPHMixValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fCPHMixValveActADSInternalValuesMirror | AT %Q* | : REAL;
fCPHMixValveSetADSInternalValuesMirror | AT %Q* | : REAL;
bCPHThrotValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fCPHThrotValveActADSInternalValuesMirror | AT %Q* | : REAL;
fCPHThrotValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Pump datapoints
eCPHPumpContModeADSInternalValuesMirror | AT %Q* | : E_PumpControlMode;
bCPHPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
bCPHPumpOperatingADSInternalValuesMirror | AT %Q* | : BOOL;
fCPHPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fCPHPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
bCPHPumpSetOnADSInternalValuesMirror | AT %Q* | : BOOL;
fCPHPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fCPHPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
fCPHPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
//DID (cealing induction unit/chilled beam) heating datapoints
//Temperature sensor datapoints
fDIDHTempSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fDIDHTempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fDIDHTempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
fDIDHTempSupADSInternalValuesMirror | AT %Q* | : REAL;
fDIDHTempRetADSInternalValuesMirror | AT %Q* | : REAL;
//Valve datapoints
bDIDHValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fDIDHValveActADSInternalValuesMirror | AT %Q* | : REAL;
fDIDHValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Pump datapoints
eDIDHPumpContModeADSInternalValuesMirror | AT %Q* | : E_PumpControlMode;
bDIDHPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
bDIDHPumpOperatingADSInternalValuesMirror | AT %Q* | : BOOL;
fDIDHPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fDIDHPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
bDIDHPumpSetOnADSInternalValuesMirror | AT %Q* | : BOOL;
fDIDHPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fDIDHPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
fDIDHPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
//DID (ceiling induction unit/chilled beam) cooling datapoints
//Temperature sensor datapoints
fDIDCTempSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fDIDCTempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fDIDCTempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
fDIDCTempSupADSInternalValuesMirror | AT %Q* | : REAL;
fDIDCTempRetADSInternalValuesMirror | AT %Q* | : REAL;
//Valve datapoints
bDIDCValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fDIDCValveActADSInternalValuesMirror | AT %Q* | : REAL;
fDIDCValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Pump datapoints
eDIDCPumpContModeADSInternalValuesMirror | AT %Q* | : E_PumpControlMode;
bDIDCPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
bDIDCPumpOperatingADSInternalValuesMirror | AT %Q* | : BOOL;
fDIDCPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fDIDCPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
bDIDCPumpSetOnADSInternalValuesMirror | AT %Q* | : BOOL;
fDIDCPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fDIDCPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
fDIDCPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
//RHAndRC (Reheater and Recooler) datapoints
//Temperature sensor datapoints
fRHARCTempSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCTempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCTempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCTempSupADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCTempRetADSInternalValuesMirror | AT %Q* | : REAL;
//Mixvalve datapoints
bRHARCRCMixValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fRHARCRCMixValveActADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCRCMixValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Throttvalve datapoints
bRHARCThrotValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fRHARCThrotValveActADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCThrotValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Three-way-Valve datapoints
bRHARCSwitchValveSupErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fRHARCSwitchValveSupActADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCSwitchValveSupSetADSInternalValuesMirror | AT %Q* | : REAL;
bRHARCSwitchValveRetErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fRHARCSwitchValveRetActADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCSwitchValveRetSetADSInternalValuesMirror | AT %Q* | : REAL;
//Pump datapoints
eRHARCpumpContModeADSInternalValuesMirror | AT %Q* | : E_PumpControlMode;
bRHARCPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
bRHARCPumpOperatingADSInternalValuesMirror | AT %Q* | : BOOL;
fRHARCPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
bRHARCPumpSetOnADSInternalValuesMirror | AT %Q* | : BOOL;
fRHARCPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
fRHARCPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
//Jet nozzle datapoints
//Volume flow controller datapoints
fJNVolumeFlowSetpoint1ADSInternalValuesMirror | AT %Q* | : REAL;
//fJNVolumeFlowSetpoint2ADSInternalValuesMirror | AT %Q* | : REAL; |  | //Dismantled
fJNVolumeFlowSetpoint3ADSInternalValuesMirror | AT %Q* | : REAL;
//fJNVolumeFlowSetpoint4ADSInternalValuesMirror | AT %Q* | : REAL; |  | //Dismantled
fJNVolumeFlowSetpoint5ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint6ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint7ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint8ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint9ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowSetpoint10ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowActual1ADSInternalValuesMirror | AT %Q* | : REAL;
//fJNVolumeFlowActual2ADSInternalValuesMirror | AT %Q* | : REAL; |  | //Dismantled
fJNVolumeFlowActual3ADSInternalValuesMirror | AT %Q* | : REAL;
//fJNVolumeFlowActual4ADSInternalValuesMirror | AT %Q* | : REAL; |  | //Dismantled
fJNVolumeFlowActual5ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowActual6ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowActual7ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowActual8ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowActual9ADSInternalValuesMirror | AT %Q* | : REAL;
fJNVolumeFlowActual10ADSInternalValuesMirror | AT %Q* | : REAL;
//Angle datapoints
fJNAngleSetpointAllADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleSetpointPotiADSInternalValuesMirror | AT %Q* | : INT;
fJNAngleSetpoint1ADSInternalValuesMirror | AT %Q* | : REAL;
//fJNAngleSetpoint2ADSInternalValuesMirror | AT %Q* | : REAL; |  | //Dismantled
fJNAngleSetpoint3ADSInternalValuesMirror | AT %Q* | : REAL;
//fJNAngleSetpoint4ADSInternalValuesMirror | AT %Q* | : REAL; |  | //Dismantled
fJNAngleSetpoint5ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleSetpoint6ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleSetpoint7ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleSetpoint8ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleSetpoint9ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleSetpoint10ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleActual1ADSInternalValuesMirror | AT %Q* | : REAL;
//fJNAngleActual2ADSInternalValuesMirror | AT %Q* | : REAL; |  | //Dismantled
fJNAngleActual3ADSInternalValuesMirror | AT %Q* | : REAL;
//fJNAngleActual4ADSInternalValuesMirror | AT %Q* | : REAL; |  | //Dismantled
fJNAngleActual5ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleActual6ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleActual7ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleActual8ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleActual9ADSInternalValuesMirror | AT %Q* | : REAL;
fJNAngleActual10ADSInternalValuesMirror | AT %Q* | : REAL;
//Hall 1 central exhaust air datapoints
//Volume flow controller datapoints
fEHAVolumeFlowSetpoint1ADSInternalValuesMirror | AT %Q* | : REAL;
fEHAVolumeFlowSetpoint2ADSInternalValuesMirror | AT %Q* | : REAL;
fEHAVolumeFlowActual1ADSInternalValuesMirror | AT %Q* | : REAL;
fEHAVolumeFlowActual2ADSInternalValuesMirror | AT %Q* | : REAL;
fPotiPositionADSInternalValuesMirror | AT %Q* | : INT; |  | //used in MAIN to increase decrease temperature Setpoint
//Air handling unit datapoints
//Flap datapoints
fAHUFlapEHAActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFlapEHASetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFlapETAActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFlapETASetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFlapODAActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFlapODASetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFlapSUPActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFlapSUPSetADSInternalValuesMirror | AT %Q* | : REAL;
//Fan datapoints
fAHUFanETASpeedActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFanETASpeedSetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFanETAVdpActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFanETAVolFlowActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFanSUPSpeedActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFanSUPSpeedSetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFanSUPVdpActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUFanSUPVolFlowActADSInternalValuesMirror | AT %Q* | : REAL;
//Temperature sensor datapoints
//fAHUTempAmbAirADSInternalValuesMirror | AT %Q* | : REAL;
fAHUTempSUPSetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUTempEHAADSInternalValuesMirror | AT %Q* | : REAL;
fAHUTempETAADSInternalValuesMirror | AT %Q* | : REAL;
fAHUTempODAADSInternalValuesMirror | AT %Q* | : REAL;
fAHUTempSUPADSInternalValuesMirror | AT %Q* | : REAL;
//Humidity sensor datapoints
fAHUHumSetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUHumEHAADSInternalValuesMirror | AT %Q* | : REAL;
fAHUHumETAADSInternalValuesMirror | AT %Q* | : REAL;
fAHUHumODAADSInternalValuesMirror | AT %Q* | : REAL;
fAHUHumSUPADSInternalValuesMirror | AT %Q* | : REAL;
//Frost protection sensor datapoints
bAHUFrostProtADSInternalValuesMirror | AT %Q* | : BOOL;
//Preheater datapoints
//Temperature sensor datapoints
fAHUPHTempSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHTempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHTempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHTempSupADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHTempRetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHTempAirOutADSInternalValuesMirror | AT %Q* | : REAL;
//Valve datapoints
bAHUPHValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fAHUPHValveActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Pump datapoints
eAHUPHPumpContModeADSInternalValuesMirror | AT %Q* | : E_PumpControlMode;
bAHUPHPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
bAHUPHPumpOperatingADSInternalValuesMirror | AT %Q* | : BOOL;
fAHUPHPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
bAHUPHPumpSetOnADSInternalValuesMirror | AT %Q* | : BOOL;
fAHUPHPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
fAHUPHPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
//Heat recovery datapoints
fAHUHRBypValveAct1ADSInternalValuesMirror | AT %Q* | : REAL;
fAHUHRBypValveAct2ADSInternalValuesMirror | AT %Q* | : REAL;
fAHUHRBypValveSetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUHRTempOutEstimatedADSInternalValuesMirror | AT %Q* | : REAL;
//Cooler datapoints
//Temperature sensor datapoints
fAHUCOTempSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOTempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOTempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOTempSupADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOTempRetADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOTempOutEstimatedADSInternalValuesMirror | AT %Q* | : REAL;
//Valve datapoints
bAHUCOValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fAHUCOValveActADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Pump datapoints
eAHUCOPumpContModeADSInternalValuesMirror | AT %Q* | : E_PumpControlMode;
bAHUCOPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
bAHUCOPumpOperatingADSInternalValuesMirror | AT %Q* | : BOOL;
fAHUCOPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
bAHUCOPumpSetOnADSInternalValuesMirror | AT %Q* | : BOOL;
fAHUCOPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
fAHUCOPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
//Reheater datapoints
//Temperature sensor datapoints
fAHURHTempSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fAHURHTempSupPrimADSInternalValuesMirror | AT %Q* | : REAL;
fAHURHTempRetPrimADSInternalValuesMirror | AT %Q* | : REAL;
fAHURHTempSupADSInternalValuesMirror | AT %Q* | : REAL;
fAHURHTempRetADSInternalValuesMirror | AT %Q* | : REAL;
//Valve datapoints
bAHURHValveErrorADSInternalValuesMirror | AT %Q* | : BOOL;
fAHURHValveActADSInternalValuesMirror | AT %Q* | : REAL;
fAHURHValveSetADSInternalValuesMirror | AT %Q* | : REAL;
//Pump datapoints
eAHURHPumpContModeADSInternalValuesMirror | AT %Q* | : E_PumpControlMode;
bAHURHPumpErrorADSInternalValuesMirror | AT %Q* | : BOOL;
bAHURHPumpOperatingADSInternalValuesMirror | AT %Q* | : BOOL;
fAHURHPumpPowerADSInternalValuesMirror | AT %Q* | : REAL;
fAHURHPumpPressureADSInternalValuesMirror | AT %Q* | : REAL;
bAHURHPumpSetOnADSInternalValuesMirror | AT %Q* | : BOOL;
fAHURHPumpSetpointADSInternalValuesMirror | AT %Q* | : REAL;
fAHURHPumpSpeedADSInternalValuesMirror | AT %Q* | : REAL;
fAHURHPumpVolFlowADSInternalValuesMirror | AT %Q* | : REAL;
//SteamHumidifier datapoints
fAHUSHSetpointADSInternalValuesMirror | AT %Q* | : REAL;
//Battery ventilation datapoints
//BAT power setpoints
fBATSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fBATEhaSetADSInternalValuesMirror | AT %Q* | : REAL;
//Bathroom ventilation datapoints
//BATH power setpoint
fBATHSupActADSInternalValuesMirror | AT %Q* | : REAL;
fBATHSupSetADSInternalValuesMirror | AT %Q* | : REAL;
fBATHEhaSetADSInternalValuesMirror | AT %Q* | : REAL;
//Hall 2 datapoints
nHALL2TempRoomADSInternalValuesMirror | AT %Q* | : INT;
bHALL2LEDADSInternalValuesMirror | AT %Q* | : BOOL;
bHALL2ButtonADSInternalValuesMirror | AT %Q* | : BOOL;
nHALL2TempOffsetADSInternalValuesMirror | AT %Q* | : INT;
nHALL2RadiationADSInternalValuesMirror | AT %Q* | : INT;
//Office room datapoints
fOFFICENoOfZonesADSInternalValuesMirror | AT %Q* | : REAL; |  | //Number of established ZoneModules
fOFFICEZoneMasterAlarmADSInternalValuesMirror | AT %Q* | : REAL; |  | //ZoneMaster alarm status
fOFFICEZoneModuleAlarmADSInternalValuesMirror | AT %Q* | : REAL; |  | //ZoneModule alarm status
fOFFICEZoneMasterOpADSInternalValuesMirror | AT %Q* | : REAL; |  | //ZoneMaster operation status
//Meeting room 2
fOFFICEe6StatusADSInternalValuesMirror | AT %Q* | : REAL; |  | //ZoneModule status
fOFFICEe6VFCETAActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) actual position
fOFFICEe6VFCSUPActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) actual position
fOFFICEe6VFCETASetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) setpoint position
fOFFICEe6VFCSUPSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) setpoint position
fOFFICEe6TempSetActualADSInternalValuesMirror | AT %Q* | : REAL; |  | //Actual temperature setpoint after considering the offset
fOFFICEe6TempOffsetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Temperature setpoint offset
fOFFICEe6TempActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current room temperature measured in the extract air (ETA)
fOFFICEe6RHActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current relative humidity (RH) measured in the extract air (ETA)
fOFFICEe6VOCActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current volatile organic compounds (VOC) measured in the extract air (ETA)
fOFFICEe6CValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Cooling valve setpoint
fOFFICEe6HValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Heating valve setpoint
//Meeting room 1
fOFFICEe5StatusADSInternalValuesMirror | AT %Q* | : REAL; |  | //ZoneModule status
fOFFICEe5VFCETAActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) actual position
fOFFICEe5VFCSUPActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) actual position
fOFFICEe5VFCETASetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) setpoint position
fOFFICEe5VFCSUPSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) setpoint position
fOFFICEe5TempSetActualADSInternalValuesMirror | AT %Q* | : REAL; |  | //Actual temperature setpoint after considering the offset
fOFFICEe5TempOffsetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Temperature setpoint offset
fOFFICEe5TempActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current room temperature measured in the extract air (ETA)
fOFFICEe5RHActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current relative humidity (RH) measured in the extract air (ETA)
fOFFICEe5VOCActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current volatile organic compounds (VOC) measured in the extract air (ETA)
fOFFICEe5CValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Cooling valve setpoint
fOFFICEe5HValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Heating valve setpoint
//Office room 2
fOFFICEe4StatusADSInternalValuesMirror | AT %Q* | : REAL; |  | //ZoneModule status
fOFFICEe4VFCETAActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) actual position
fOFFICEe4VFCSUPActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) actual position
fOFFICEe4VFCETASetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) setpoint position
fOFFICEe4VFCSUPSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) setpoint position
fOFFICEe4TempSetActualADSInternalValuesMirror | AT %Q* | : REAL; |  | //Actual temperature setpoint after considering the offset
fOFFICEe4TempOffsetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Temperature setpoint offset
fOFFICEe4TempActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current room temperature measured in the extract air (ETA)
fOFFICEe4RHActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current relative humidity (RH) measured in the extract air (ETA)
fOFFICEe4VOCActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current volatile organic compounds (VOC) measured in the extract air (ETA)
fOFFICEe4CValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Cooling valve setpoint
fOFFICEe4HValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Heating valve setpoint
//Office room 1
fOFFICEe3StatusADSInternalValuesMirror | AT %Q* | : REAL; |  | //ZoneModule status
fOFFICEe3VFCETAActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) actual position
fOFFICEe3VFCSUPActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) actual position
fOFFICEe3VFCETASetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) setpoint position
fOFFICEe3VFCSUPSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) setpoint position
fOFFICEe3TempSetActualADSInternalValuesMirror | AT %Q* | : REAL; |  | //Actual temperature setpoint after considering the offset
fOFFICEe3TempOffsetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Temperature setpoint offset
fOFFICEe3TempActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current room temperature measured in the extract air (ETA)
fOFFICEe3RHActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current relative humidity (RH) measured in the extract air (ETA)
fOFFICEe3VOCActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current volatile organic compounds (VOC) measured in the extract air (ETA)
fOFFICEe3CValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Cooling valve setpoint
fOFFICEe3HValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Heating valve setpoint
//Workshop room
fOFFICEe2StatusADSInternalValuesMirror | AT %Q* | : REAL; |  | //ZoneModule status
fOFFICEe2VFCETAActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) actual position
fOFFICEe2VFCSUPActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) actual position
fOFFICEe2VFCETASetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) extract air (ETA) setpoint position
fOFFICEe2VFCSUPSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Volume flow controller (VFC) supply air (SUP) setpoint position
fOFFICEe2TempSetActualADSInternalValuesMirror | AT %Q* | : REAL; |  | //Actual temperature setpoint after considering the offset
fOFFICEe2TempOffsetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Temperature setpoint offset
fOFFICEe2TempActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current room temperature measured in the extract air (ETA)
fOFFICEe2RHActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current relative humidity (RH) measured in the extract air (ETA)
fOFFICEe2VOCActADSInternalValuesMirror | AT %Q* | : REAL; |  | //Current volatile organic compounds (VOC) measured in the extract air (ETA)
fOFFICEe2CValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Cooling valve setpoint
fOFFICEe2HValveSetADSInternalValuesMirror | AT %Q* | : REAL; |  | //Heating valve setpoint